## Slide 1: Bush River 115kV Crossing Rebuild
Tiffany Matthews-Lay
Project Management

## Slide 2: Proposed Bush River Project
Rebuild the Bush River Crossing
  Remove 7 existing “lattice” structures
  Install 9 new mono-pole structures and foundations
  One structure located in Bush River
  New conductor
  1.3 miles long
  Additional easements required
  Construction starts September 2021
  In-Service Date: May 2022
Bush River Crossing

## Slide 3: Project Necessity
BGE has the responsibility to maintain safety and the reliability of its electric system, achieved through routine inspection and maintenance of its existing transmission lines.
  Inspections identified the transmission line at the Bush River Crossing (Circuits 110620/110621) as a priority transmission circuit in the BGE system.
  Inspections identified seven (7) existing structures that require replacement.
Improve reliability and safety of the transmission line for communities and critical infrastructure.
  This line connects three substations, one of which serves 12,500 customers and one serves APG critical infrastructure directly.
The existing transmission line consists of two circuits constructed in 1951 and has experienced substantial reliability and risk issues.
  Severe avian contamination
  Severe foundation degradation was discovered after an inspection in 1991
  Mariner safety

## Slide 4: Structural Reliability and Safety
In 1991, these tower foundations were inspected, and severe degradation was discovered.
Although repairs were made in 1991, those repairs are now in year 30 of an expected 25-year life span.

## Slide 5: Avian Challenges
9 outages (2009-2019) were line-initiated, all 9 occurred within the Bush River Crossing
  8 outages were related to avian interference
    7 outages involved bird nest debris
    1 outage involved bird droppings
  1 unknown outage
Momentary outage on 5/10/2017 led to the discovery of a large colony of cormorants
  Numerous nests
  Significant contamination found on the insulators, conductors, tower steel, and foundations
  According to the USDA-APHIS, there are no totally effective ways to keep the cormorants from inhabiting the tower

## Slide 6: Avian Challenges (cont.)
During the inspection, an active osprey nest was also found on tower 56 (Perryman side).
Insulators were replaced and “guano shields” were installed, but due to the liquid state of the contaminant and the steady wind, the shields were not entirely effective.
Coexisting with cormorants means accessing a severely “contaminated” tower, maneuvering around mildly aggressive birds, and maintaining insulators and conductors that will continue to become contaminated.

## Slide 7: Boat Safety
The existing line has a low clearance over the Bush River.
The line has had a history of sailboat contacts, the most recent of which was in August 2000.

## Slide 8: Proposed Solution
Removal
  Three double circuit steel lattice towers (one on each shore and one located within Bush River)
  Four single circuit wood H-frames (two on each side of the river)
  Existing conductor (4 spans total)
N
Install
  4 new single circuit structures at each bank
  1 double circuit structure at mid-span in Bush River on pile foundation
  New section will be built parallel to the existing line to minimize outage impacts
  Design clearance of 49.1 ft (40 ft safe vessel height)

## Slide 9: Proposed Solution – Each Bank
Install
  4 new single circuit structures at each bank
  New conductor (4 spans)
  Caisson foundations on land
  Pole caps will be used to deter birds from nesting on structures
Removal
  Three double circuit steel lattice towers (one on each shore and one located within Bush River)
  Four single circuit wood H-frames (two on each side of the river)
  Existing conductor (4 spans total)

## Slide 10: Environmental Mitigation
BGE is developing mitigation plans with Harford County and the Maryland Department of Environment and Department of Natural Resources to address:
  Restoring areas where existing structures are removed
  Planting new trees
  Restoring the Critical Area Buffer
  Requiring contractor to use Best Management Practices during construction activities
  Ensuring the construction schedule takes the wildlife impact into consideration

## Slide 11: Renderings

## Slide 12: Project Website
https://www.bge-tsrep.com/projects/bush-river-crossing/